## Slide 1: OpenIPSL A Modelica Library for Power Systems Simulation
Assoc. Prof. Luigi Vanfretti
luigiv@kth.se,
https://www.kth.se/profile/luigiv/
Hands-on Examples!
Please follow these slides to carry out the examples.
Notes: Airport to central station
Take line 3 or line 4 to Nyl… (Stattnet)

## Slide 2: Workshop Agenda
Very brief introduction to the Open-Instance Power System Library
Modelling and simulation possibilities by using OpenIPSL and Modelica
Comparison of the performance with a reference simulation software
3 use cases with a dynamic simulation and linearization

## Slide 3: Download the files for the tutorial:
Go to our Github repo:
https://github.com/SmarTS-Lab/OpenIPSL/releases/tag/Tuto_TAMU_2017
Note: A dedicated package will be prepared for the tutorial and uploaded soon.
Please download (again!) the package on the day of the tutorial so that you have the most up to date files.
The dedicated package will also be available on a USB stick that we can circulate on the day of the tutorial.
Click Here!

## Slide 4: Load the OpenIPSL to OMEdit
External libraries, such as OpenIPSL, must be loaded in OMEdit to be used:
Unzip the package downloaded at the previous step
Open OpenModelica Connection Editor (OMEdit)
Browse Windows Explorer to the location of the unzipped folder
Drag & drop the OpenIPSL.mo file to the Library Browser in OMEdit.

## Slide 5: Load an Application Example to OMEdit
Once the OpenIPSL is loaded (see previous slide) in OMEdit, you can load the Tutorial package:
Browse Windows Explorer to the location of the unzipped folder
Drag & drop the Tutorial.mo file to the Library Browser in OMEdit.

## Slide 6: Library introduction
OpenIPSL is divided in four main categories:

## Slide 7: Library introduction
Electrical
The Electrical package contains most of the components that comprise an actual power network
E.g., electrical machines, transmission lines, loads, excitation systems, turbine governors, etc.
These are used to build the power system network models

## Slide 8: Library introduction
NonElectrical
The NonElectrical package is comprised by functions, blocks or models, which are used to build the aforementioned power system component models : Transfer functions, logical operators, etc.
They perform specific operations which were not available in the Modelica Standard Library (MSL)
Connectors
The Connectors package contains a set of specifically developed Modelica connectors to harmonize the models in this library ( e.g. PwPin a connector, which contains voltage and current quantities in phasor representation)

## Slide 9: Library introduction
Examples
In this workshop, the Tutorial package will be used to showcase the possibilities of the library
In the packages Example_1, Example_2 and Example_3 prepared use cases can be found where steps to build the models are described
Package Working_Examples and corresponding sub-packages will be used by attendees of the workshop to create use cases on their own

## Slide 10: Example 1*
Single Machine Infinite Bus (SMIB) system
Analysis of the transient stability of the system including the effects of rotor circuit dynamics and excitation control
Four machines represented by one connected via transformer and parallel lines to the infinite bus
* P. Kundur, “Power System Stability and Control”, Example 13.2

## Slide 11: Example 1
Power flow
Power flow results were obtained by PSAT
Prepared Example 1 already exists in PSAT and can be used for power flow calculations and dynamic simulations

## Slide 12: Example 1
Power flow
Example 1 is loaded and the power flow calculations are executed

## Slide 13: Example 1
Power flow
Static Report can be access where all of the power flow results are listed along with the initial values of various state variables of the models
In this tutorial, there is no need to run the power flow in PSAT since the data will be provided, but feel free to explore PSAT later

## Slide 14: Example 1
Power flow
The summary of all of the relevant data from the power flow is given on the figure below

## Slide 15: Example 1
Generator model – Step 1
First, the package where the generator model will be located has to be created
This is done by right clicking on the Example_1 in the Working_Examples package
The package should be named Generator

## Slide 16: Example 1
Generator model – Step 1
Within the Generator package, model of the generator shall be created
Extends from Tutorial.Support.Generator_Example

## Slide 17: Example 1
Generator model – Step 1
6th order model of the generator from the PSAT is used
The model is added by dragging the generator from the library and dropping it to the model

## Slide 18: Example 1
Generator model – Step 1
Parameters of the generator are given in the table
 | 2220 |  | 0.25
 | 400 |  | 8
 | 0.003 |  | 1
 | 1.81 |  | 0.03
 | 1.76 |  | 0.07
 | 0.3 |  | 0.002
 | 0.65 |  | 7
 | 0.23 |  | 0
 | 2220 |  | 0.25
 | 400 |  | 8
 | 0.003 |  | 1
 | 1.81 |  | 0.03
 | 1.76 |  | 0.07
 | 0.3 |  | 0.002
 | 0.65 |  | 7
 | 0.23 |  | 0

## Slide 19: Example 1
Generator model – Step 1
Power flow results:
Note: Using the variables (V_0, angle_0, etc.) allow to propagate the parameters to the “upper layer” of the generator component
 | V_0
 | angle_0
 | P_0
 | Q_0
 | V_b
 | Do not edit
 | Do not edit
 | V_0
 | angle_0
 | P_0
 | Q_0
 | V_b
 | Do not edit
 | Do not edit

## Slide 20: Example 1
Generator model – Step 2
PSAT model of the AVR Type III is used
Constant block pss_off will be used as a zero input to the PSS input signal of the AVR since the PSS is not used
Parameters:
 | 7
 | -6.4
 | 200
 | 1
 | 1
 | 0.0001
 | 0.015
 | 7
 | -6.4
 | 200
 | 1
 | 1
 | 0.0001
 | 0.015

## Slide 21: Example 1
Generator model – Step 3
To finish the generator model, different signals need to be connected
Optionally, icon of the generator model can be altered

## Slide 22: Example 1
Network model – Step 1
Network package will be created in the Example_1 package
This package is created by right clicking on the Example_1 in the Working_Examples package

## Slide 23: Example 1
Network model – Step 1
Network model will be created in the Network package
This package is created by right clicking on the Network package
The name of the network model will be Example_1

## Slide 24: Example 1
Network model – Step 1
Created generator model (name it machine) and three bus models are added to the network model
Also, model OpenIPSL.Electrical.SystemBase shall be added to the network model which defines base parameters for all of the components in the network model
In text view add the inner keyword in front of the component declaration
 | 100
 | 60
 | 100
 | 60

## Slide 25: Example 1
Network model – Step 2
Transformer and line models are added

## Slide 26: Example 1
Network model – Step 2
Transformer and line parameters
Transformer
 | 0.0 |  | 0.0
 | 0.5*100/2220 |  | 0.0
 | 100 |  | 
 | 0.0 |  | 0.0
 | 0.5*100/2220 |  | 0.0
 | 100 |  | 
Line 1
 | 0.0 |  | 0.0
 | 0.93*100/2220 |  | 0.0
 | 100 |  | 
 | 0.0 |  | 0.0
 | 0.93*100/2220 |  | 0.0
 | 100 |  | 
Line 2
 | Do not edit |  | Do not edit
 | 2220 |  | 1
 | 400 |  | 0.15
 | 400 |  | 0
 | Do not edit |  | Do not edit
 | 2220 |  | 1
 | 400 |  | 0.15
 | 400 |  | 0

## Slide 27: Example 1
Network model – Step 3
Infinite bus is added
Power Flow results are implemented
 | 0.90081 |  | 0
P | -1998 | Q | 87.066
 | 0.90081 |  | 0
P | -1998 | Q | 87.066
Infinite bus
 | 1 |  | 0.4946
P | 1997.999 | Q | 967.92
 | 1 |  | 0.4946
P | 1997.999 | Q | 967.92
G1

## Slide 28: Example 1
Network model – Step 4
3-phase-to-ground fault is added
 | 0 |  | 0.5
 | 0.01*100/2220 |  | 0.57
 | 0 |  | 0.5
 | 0.01*100/2220 |  | 0.57
Fault

## Slide 29: Example 1
Network model – Step 5
The network model is completed by connecting all of the components
Now, the model can be simulated and linearized

## Slide 30: Example 1
Simulation
System will be simulated with 3-phase-to-ground fault at t=0.5s with a duration of 70ms
Simulation results will be compared with the reference results from the PSAT that will be loaded first
PSAT results are provided in a file “PSAT_dyn.csv”
To load the file, the view should be switched to “Plotting” tab

## Slide 31: Example 1
Simulation
Result file can be opened by navigating the menu to File->Open Result File(s)
In the pop-up menu, one has to select “Comma Separated Values” as a file type, navigate to the directory where the file is located and open it

## Slide 32: Example 1
Simulation
In the variable browser, three waveforms from the PSAT results are loaded which can be displayed on the plot as it is shown in the figure below
Loaded waveforms are generator terminal voltage, excitation field voltage and the generator speed

## Slide 33: Example 1
Simulation
Before the simulation, solver and its parameters are set to be the same as in the PSAT
Solver is chosen to be Runge-Kutta with a fixed step
More solvers can be chosen in Modelica (depending on the tool), however, to match the model’s response with the one in PSAT choice of the solver is limited

## Slide 34: Example 1
Simulation
Simulation time is set to 10s and the tolerance of the solver is set to 1e-6
The time step is set to 0.0001

## Slide 35: Example 1
Simulation
By pressing the “Simulate” button on the toolbar, simulation of the model is executed
Once the simulation is completed, the Variable Browser is populated with the simulation results

## Slide 36: Example 1
Simulation
To display the simulation results or compare it with the results from PSAT, one can mark the check-box next to the variable which will be shown on the plot
To show the terminal voltage of the generator in PSAT and modelica, variables “PSAT_dyn.v” and “Example_1.G1.machine.v” have to be selected

## Slide 37: Example 1
Simulation
To display the simulation results or compare it with the results from PSAT, one can mark the check-box next to the variable which will be shown on the plot
To show the terminal voltage of the generator in PSAT and modelica, variables “PSAT_dyn.csv.v” and “G1.machine.v” have to be selected

## Slide 38: Example 1
Simulation
To be able to distinguish different signals, let’s adjust the thickness and the pattern of the signal line

## Slide 39: Example 1
Simulation
Previous steps produce the plot shown in the figure below showing that the Modelica produces the same simulation results as the PSAT does

## Slide 40: Using OMNotebook for Interactive Analysis
The OpenModelica installation includes a very handy tool called OMNotebook.
OMNotebook allows you to interact with the OpenModelicaCompiler (OMC), and at the same time analyze the model. This gives you a basic “lab notebook” where you do your tests before you create a script for automated analysis (called .mos scripts).
We use OMNotebook next to load the model developed, and simulate it interactively.

## Slide 41: Loading and Simulating your Model
Set your patch to where your tutorial .zip is available.
Evaluate each cell using “Shift+Enter”
Instantiate and Simulate the Model

## Slide 42: Plotting in OMNotebook

## Slide 43: Parametric Sweep and Simulation using OMNotebook
Using OMNotebook, we can interact with the OMC in order to analyze the behavior of the system.
The AVR’s output looks saturated.
The type of instability that we are observing it is typically due to negative feedback from the AVR. This was shown in the early 1900’s by Concordia and De Mello!
A parametric sweep is used in OMC to simulate the system’s response for different values of the gain of the AVR, namely, K0.

## Slide 44: Parametric Sweep and Simulation using OMNotebook

## Slide 45: Parametric Sweep and Simulation using OMNotebook
K0 = 50
K0 = 10

## Slide 46: Parametric Sweep and Simulation using OMNotebook

## Slide 47: Linear Analysis
Let’s now do a bit more analysis on the system’s stability by using linear analysis.
This will allow us to determine the system’s damping with the current value of the AVR’s gain (K=200).
Two methods are shown in the following slides, using OMNotebook and the OMShell (optional).

## Slide 48: Linear Analysis

## Slide 49: Linear Analysis

## Slide 50: Example 1 – Linearization using OMShell
Linearization
To linearize the system, OpenModelica scripting will be needed
Along with the library, a set of commands was provided (Command_List.txt) to linearize the model and extract the A matrix

## Slide 51: Example 1 – Linearization using OMShell
Linearization
Copy and paste each line from the Command_List.txt for Example 1 to the command prompt in OpenModelica

## Slide 52: Example 1 – Linearization using OMShell
Linearization
The third command will save the A matrix of the linearized state-space model in the variable a as a string

## Slide 53: Example 1 – Linearization using OMShell
Linearization
Copy the output from the previous command without the quotation marks by pressing Ctrl+C

## Slide 54: Example 1 – Linearization using OMShell
Linearization
To save the matrix A as a matrix of Real values type A := and then press Ctrl+V to paste the copied matrix

## Slide 55: Example 1 – Linearization using OMShell
Linearization
It is known that the eigenvalues of the linearized system can be found by solving the following equation:
This can be done by executing the last command (eval,evec) := Modelica.Math.Matrices.eigenValues(A);

## Slide 56: Example 1 – Linearization using OMShell
Linearization
The eigenvalues are now stored in the eval variable and they can be listed by executing eval
Groups of numbers are listed where the first number is real part of the system’s pole and the second one is the imaginary part

## Slide 57: Example 1 – Linearization using OMShell
Linearization
It can be seen that the pair of conjugate poles exists on the right side of the stability plane and thus, the behavior of the system is unstable

## Slide 58: Example 2
In the Example 1, it was shown that the system was unstable with a pair of poles on the right side of the stability plane
In the Example 2, Power System Stabilizer (PSS) will be added to the generator in order to stabilize the system

## Slide 59: Example 2
The work on Example 2 should continue with the files prepared in a package Tutorial.Working_Examples.Example_2

## Slide 60: Example 2
Generator model – Step 1
The first step is to add the model of the PSS Type II and the summation block to the model of the generator

## Slide 61: Example 2
Generator model – Step 1
The internal control structure of the PSS can be accessed by right-clicking on the PSS block and selecting “View Class”

## Slide 62: Example 2
Generator – Step 1
PSS should be parameterized as shown in the table
PSS
 | 0.2 |  | 0.154
 | -0.2 |  | 0.033
 | 9.5 |  | 1
 | 1.41 |  | 1
 | 0.2 |  | 0.154
 | -0.2 |  | 0.033
 | 9.5 |  | 1
 | 1.41 |  | 1

## Slide 63: Example 2
Generator – Step 2
When the signals of the generator model are connected as shown, model of the generator is completed

## Slide 64: Example 2
Simulation
Simulation steps can be repeated as it was shown in the Example 1
This time, reference simulation results from the PSAT can be found in the file “PSAT_dyn_PSS.csv”
After the simulation is executed, variable browser should look as it is shown below

## Slide 65: Example 2
Simulation
Simulation results can be plotted again
Comparison of the PSAT and Modelica simulation results of the PSS signal is shown on the figure below

## Slide 66: Example 2
Linearization
To linearize the system, OpenModelica scripting will be needed
Along with the library, a set of commands was provided (Command_List.txt) to linearize the model and extract the A matrix

## Slide 67: Example 1
Linearization
Copy and paste each line from the Command_List.txt for Example 1 to the command prompt in OpenModelica

## Slide 68: Example 2
Linearization
The rest of the steps shall be repeated as it was shown in Example 1
The same procedure with a linearized system from Example 2 results in the new set of eigenvalues

## Slide 69: Example 2
Linearization
The conjugate pair of poles that was on the right side of the plane in Example 1 was, by introducing the PSS, moved to the left side of the stability plane and, thus, the system is now stable

## Slide 70: Example 3

## Slide 71: Example 3
Example 3 contains the model of the IEEE 9 Bus system
It is pre-configured with all of the power flow and dynamic data
In the previous two examples, you learned how to build the models of the power system, introduce the faults, run the dynamic simulations and perform the linearization of the model
In Example 3 you are free to explore the model and introduce various faults

## Slide 72: Example 3
You can, for instance, introduce the bus fault …

## Slide 73: Example 3
... or open the line at the given time instant*
*Model of the line with opening is OpenIPSL.Electrical.Branches.PwLine2Openings

## Slide 74: Example 3
Step disturbance to the voltage reference of the generators can be introduced by setting the desired refdisturb_x parameter to true

## Slide 75: Questions?
Luigi Vanfretti
Tin Rabuzin
Achour Amazouz
Mohammed Ahsan Adib Murad
Francisco José Gómez
Jan Lavenius
Le Qi
Maxime Baudette
Mengjia Zhang
Tetiana Bogodorova
Giusseppe Laera
Joan Russiñol Mussons
Thanks to all current and former OpenIPSL Developers @ KTH
Join us!