## Slide 1: OpenIPSL Tutorial A Modelica Library for Power Systems Simulation
Tin Rabuzin and Assoc. Prof. Luigi Vanfretti
luigiv@kth.se,
https://www.kth.se/profile/luigiv/
Notes: Airport to central station
Take line 3 or line 4 to Nyl… (Stattnet)

## Slide 2: Aim of the workshop
Introduction to the Open-Instance PowerSystems Library
Modelling and simulation possibilities by using OpenIPSL and Modelica
Comparison of the performance with a reference simulation software
3 use cases with a dynamic simulation and linearization

## Slide 3: Library introduction
OpenIPSL is divided in four main categories:
Examples
Electrical
NonElectrical
Connectors
Math
Logical
Continuous
Nonlinear
Functions
Machines
Branches
Loads
Banks
Sensors
Events
Solar
Buses
Controls
Wind
OpenIPSL
NonElectrical
Electrical
Connectors
Examples

## Slide 4: Library introduction
Electrical
The Electrical package contains most of the components that comprise an actual power network
E.g., electrical machines, transmission lines, loads, excitation systems, turbine governors, etc.
These are used to build the power system network models

## Slide 5: Library introduction
NonElectrical
The NonElectrical package is comprised by functions, blocks or models, which are used to build the aforementioned power system component models
Transfer functions, logical operators, etc.
They perform specific operations which were not available in the Modelica Standard Library (MSL)

## Slide 6: Library introduction
Connectors
The Connectors package contains a set of specifically developed Modelica connectors to harmonize the models in this library
As an example, PwPin is the connector, which contains voltage and current quantities in phasor representation

## Slide 7: Library introduction
Examples
In this workshop, Tutorial package will be used to showcase the possibilities of the library
In the packages Example_1, Example_2 and Example_3 prepared use cases can be found where steps to build the models are described
Package Working_Examples and corresponding subpackages will be used by attendees of the workshop to create use cases on their own

## Slide 8: OMEdit and OpenIPSL
OpenIPSL along with the additional files should be downloaded from:
Downloaded content should be placed on C:\OpenIPSL_Tutorial

## Slide 9: OMEdit and OpenIPSL
The workshop will be carried out in OpenModelica Connection Editor (OMEdit)
The start screen of OMEdit should look like the one shown on the figure

## Slide 10: OMEdit and OpenIPSL
To open the OpenIPSL one should go to File->Open Model/Library File(s) and navigate to the OpenIPSL file that should be located in C:/OpenPSL_Workshop/OpenIPSL.mo
Also, Tutorial package should be opened which is located in C:/OpenPSL_Workshop/Tutorial.mo

## Slide 11: OMEdit and OpenIPSL
Now the library is loaded and its structure can be browsed in the Libraries Browser

## Slide 12: Example 1*
* P. Kundur, “Power System Stability and Control”, Example 13.2
Single Machine Infinite Bus (SMIB) system
Analysis of the transient stability of the system including the effects of rotor circuit dynamics and excitation control
Four machines represented by one connected via transformer and parallel lines to the infinite bus

## Slide 13: Example 1
Power flow
Power flow results were obtained by PSAT
Prepared Example 1 already exists in PSAT and can be used for power flow calculations and dynamic simulations

## Slide 14: Example 1
Power flow
Example 1 is loaded and the power flow calculations are executed

## Slide 15: Example 1
Power flow
Static Report can be access where all of the power flow results are listed along with the initial values of various state variables of the models
In this tutorial, there is no need to run the power flow in PSAT since the data will be provided, but feel free to explore PSAT later

## Slide 16: Example 1
Power flow
The summary of all of the relevant data from the power flow is given on the figure below

## Slide 17: Example 1
Generator model – Step 1
First, the package where the generator model will be located has to be created
This is done by right clicking on the Example_1 in the Working_Examples package
The package should be named Generator

## Slide 18: Example 1
Generator model – Step 1
Within the Generator package, model of the generator shall be created

## Slide 19: Example 1
Generator model – Step 1
6th order model of the generator from the PSAT is used
The model is added by dragging the generator from the library and dropping it to the model

## Slide 20: Example 1
Generator model – Step 1
Parameters of the generator are given in the table
 | 2220 |  | 0.25
 | 400 |  | 8
 | 0.003 |  | 1
 | 1.81 |  | 0.03
 | 1.76 |  | 0.07
 | 0.3 |  | 0.002
 | 0.65 |  | 7
 | 0.23 |  | 0
 | 2220 |  | 0.25
 | 400 |  | 8
 | 0.003 |  | 1
 | 1.81 |  | 0.03
 | 1.76 |  | 0.07
 | 0.3 |  | 0.002
 | 0.65 |  | 7
 | 0.23 |  | 0

## Slide 21: Example 1
Generator model – Step 1
Power flow results:
 | 1
 | 0.4946
 | 199.799
 | 96.792
 | 400
 | Do not edit
 | Do not edit
 | 1
 | 0.4946
 | 199.799
 | 96.792
 | 400
 | Do not edit
 | Do not edit

## Slide 22: Example 1
Generator model – Step 2
PSAT model of the AVR Type III is used
Constant block pss_off will be used as a zero input to the PSS input signal of the AVR since the PSS is not used
Parameters:
 | 1 |  | 1
 | 1 |  | 0.0001
 | 7 |  | 0.015
 | -6.4 |  | 
 | 200 |  | 
 | 1 |  | 
 | 1 |  | 1
 | 1 |  | 0.0001
 | 7 |  | 0.015
 | -6.4 |  | 
 | 200 |  | 
 | 1 |  | 

## Slide 23: Example 1
Generator model – Step 3
Additional PwPin will be used to interface generator model’s voltages and currents with other components of the network model

## Slide 24: Example 1
Generator model – Step 4
To finish the generator model, different signals need to be connected
Optionally, icon of the generator model can be altered

## Slide 25: Example 1
Network model – Step 1
Network package will be created in the Example_1 package
This package is created by right clicking on the Example_1 in the Working_Examples package

## Slide 26: Example 1
Network model – Step 1
Network model will be created in the Network package
This package is created by right clicking on the Network package
The name of the network model will be Example_1

## Slide 27: Example 1
Created generator model and three bus models are added to the network model
Also, model OpenIPSL.Electrical.SystemBase shall be added to the network model which defines base parameters for all of the components in the network model
Network model – Step 1
 | 100
 | 60
 | 100
 | 60

## Slide 28: Example 1
Network model – Step 2
Transformer and line models are added

## Slide 29: Example 1
Network model – Step 2
 | - |  | -
 | 2220 |  | 1
 | 60 |  | 0.15
 | 0.001 |  | 0
 | - |  | -
 | 2220 |  | 1
 | 60 |  | 0.15
 | 0.001 |  | 0
Transformer and line parameters
Transformer
 | 0.0 |  | 0.0
 | 0.5*100/2220 |  | 0.0
 | 100 |  | 
 | 0.0 |  | 0.0
 | 0.5*100/2220 |  | 0.0
 | 100 |  | 
Line 1
 | 0.0 |  | 0.0
 | 0.93*100/2220 |  | 0.0
 | 100 |  | 
 | 0.0 |  | 0.0
 | 0.93*100/2220 |  | 0.0
 | 100 |  | 
Line 2

## Slide 30: Example 1
Network model – Step 3
Infinite bus is added
 | 0.90081 |  | 0
P | -1998 | Q | 87.066
 | 0.90081 |  | 0
P | -1998 | Q | 87.066
Infinite bus

## Slide 31: Example 1
Network model – Step 4
3-phase-to-ground fault is added
 | 0 |  | 0.5
 | 0.01*100/2220 |  | 0.57
 | 0 |  | 0.5
 | 0.01*100/2220 |  | 0.57
Fault

## Slide 32: Example 1
Network model – Step 5
The network model is completed by connecting all of the components
Now, the model can be simulated and linearized

## Slide 33: Example 1
Simulation
System will be simulated with 3-phase-to-ground fault at t=0.5s with a duration of 70ms
Simulation results will be compared with the reference results from the PSAT that will be loaded first
PSAT results are provided in a file “PSAT_dyn.csv”
To load the file, the view should be switched to “Plotting” tab

## Slide 34: Example 1
Simulation
Result file can be opened by navigating the menu to File->Open Resut File(s)
In the pop-up menu, one has to select “Comma Separated Values” as a file type, navigate to the directory where the file is located and open it

## Slide 35: Example 1
Simulation
In the variable browser, three waveforms from the PSAT results are loaded which can be displayed on the plot as it is shown in the figure below
Loaded waveforms are generator terminal voltage, excitation field voltage and the generator speed

## Slide 36: Example 1
Simulation
Before the simulation, solver and its parameters are set to be the same as in the PSAT
Solver is chosen to be Runge-Kutta with a fixed step
More solvers can be chosen in Modelica (depending on the tool), however, to match the model’s response with the one in PSAT choice of the solver is limited

## Slide 37: Example 1
Simulation
Simulation time is set to 10s and the tolerance of the solver is set to 1e-6
The time step is set to 0.0001

## Slide 38: Example 1
Simulation
By pressing the “Simulate” button on the toolbar, simulation of the model is executed
Once the simulation is completed, Variable Browser is populated with the simulation results

## Slide 39: Example 1
Simulation
To display the simulation results or compare it with the results from PSAT, one can mark the check-box next to the variable which will be shown on the plot
To show the terminal voltage of the generator in PSAT and modelica, variables “PSAT_dyn.v” and “Example_1.G1.machine.v” have to be selected

## Slide 40: Example 1
Simulation
To display the simulation results or compare it with the results from PSAT, one can mark the check-box next to the variable which will be shown on the plot
To show the terminal voltage of the generator in PSAT and modelica, variables “PSAT_dyn.csv.v” and “G1.machine.v” have to be selected

## Slide 41: Example 1
Simulation
To be able to destinguish different signals, one should adjust the thickness and the patter of the signal line

## Slide 42: Example 1
Simulation
Previous steps produce the plot shown in the figure below showing that the Modelica produces the same simulation results as the PSAT does

## Slide 43: Example 1
Linearization
To linearize the system, OpenModelica scripting will be needed
Along with the library, script linearize_OpenIPSL.mos was provided which performs the linearization procedure and provides the A matrix from the linearized state-space model
The scripting shall be done in the command line interface of OpenModelica called OMShell

## Slide 44: Example 1
Linearization
First, open the script linearize_OpenIPSL.mos with a text editor and make sure that the path in the second line points to the OpenIPSL distribution on your hard drive
On Mac: /Applications/MacPorts/Contents/OMShell
>>cd("/Users/luigiv/Downloads/2016_05_ENTSOE_Tutorial")
>>loadFile(“OpenIPSL.mo”)
>>loadFile(“Tutorial.mo”)
>>linearize(Tutorial.Example_1.Example_1,stopTime=0)
The file with the linearized model is given as an output linear_*name*.mo
>>loadFile(“linear_Tutorial.Example_1.Example_1.mo”);
>>(a) := getParameterValue(linear_Tutorial_Example__1__1,”A”)

## Slide 45: Example 1
Linearization
To linearize system, Modelica script linearize_OpenIPSL.mos is run by executing a command runScript(“C:/OpenIPSL_Tutorial/linearize_OpenIPSL.mos”)

## Slide 46: Example 1
Linearization
Upon the execution, the A matrix of the linearized state-space model will be saved in the variable a as a string
By typing a and pressing Enter, it will be displayed

## Slide 47: Example 1
Linearization
Copy the output from the previous command without the quotation marks by pressing Ctrl+C

## Slide 48: Example 1
Linearization
To save the matrix A as a matrix of Real values type A := and then press Ctrl+V to paste the copied matrix

## Slide 49: Example 1
Linearization
It is known that the eigenvalues of the linearized system can be found by solving the following equation:
This can be done by executing command (eval,evec) := Modelica.Math.Matrices.eigenValues(A);

## Slide 50: Example 1
Linearization
The eigenvalues are now stored in the eval variable and they can be listed by executing eval
Groups of numbers are listed where the first number is real part of the system’s pole and the second one is the imaginary part

## Slide 51: Example 1
Linearization
It can be seen that the pair of conjugate poles exists on the right side of the stability plane and thus, the behaviour of the system is unstable

## Slide 52: Example 2
In the Example 1, it was shown that the system was unstable with a pair of poles on the right side of the stability plane
In the Example 2, Power System Stabilizer (PSS) will be added to the generator in order to stabilize the system

## Slide 53: Example 2
The work on Example 2 should continue with the files prepared in a package Tutorial.Working_Examples.Example_2

## Slide 54: Example 2
Generator model – Step 1
The first step is to add the model of the PSS Type II and the summation block to the model of the generator

## Slide 55: Example 2
Generator model – Step 1
The internal control structure of the PSS can be accessed by right-clicking on the PSS block and selecting “View Class”

## Slide 56: Example 2
Generator – Step 1
PSS should be parameterized as shown in the table
 | 0.2 |  | 0.154
 | -0.2 |  | 0.033
 | 1.41 |  | 1
 | 0.001 |  | 1
 | 0.2 |  | 0.154
 | -0.2 |  | 0.033
 | 1.41 |  | 1
 | 0.001 |  | 1
PSS

## Slide 57: Example 2
Generator – Step 2
When the signals of the generator model are connected as shown, model of the generator is completed

## Slide 58: Example 2
Simulation
Simulation steps can be repeated as it was shown in the Example 1
This time, reference simulation results from the PSAT can be found in the file “PSAT_dyn_PSS.csv”
After the simulation is executed, variable browser should look as it is shown below

## Slide 59: Example 2
Simulation
Simulation results can be plotted again
Comparison of the PSAT and Modelica simulation results of the PSS signal is shown on the figure below

## Slide 60: Example 2
Linearization
Before the system is linearized again, changes to the linearize_OpenPSL.mos script shall be made
Make sure to change the example number from 1 to 2 in lines 4-10
The script should look as it is shown on the figure below

## Slide 61: Example 2
Linearization
The rest of the steps shall be repeated as it was shown in Example 1
The same procedure with a linearized system from Example 2 results in the new set of eigenvalues

## Slide 62: Example 2
Linearization
The conjugate pair of poles that was on the right side of the plane in Example 1 was, by introducing the PSS, moved to the left side of the stability plane and, thus, the system is now stable

## Slide 63: Example 3

## Slide 64: Example 3
Example 3 contains the model of the IEEE 9 Bus system
It is pre-configured with all of the power flow and dynamic data
In the previous two examples, you learned how to build the models of the power system, introduce the faults, run the dynamic simulations and perform the linearization of the model
In Example 3 you are free to explore the model and introduce various faults

## Slide 65: Example 3
You can, for instance, introduce the bus fault …

## Slide 66: Example 3
... or open the line at the given time instant*
*Model of the line with opening is OpenIPSL.Electrical.Branches.PwLine2Openings

## Slide 67: Example 3
Step disturbance to the voltage reference of the generators can be introduced by setting the desired refdisturb_x parameter to true

## Slide 68: Questions? Thanks to all current and former OpenIPSL Developers @ KTH
Luigi Vanfretti
Tin Rabuzin
Achour Amazouz
Mohammed Ahsan Adib Murad
Francisco José Gómez
Jan Lavenius
Le Qi
Maxime Baudette
Mengjia Zhang
Tetiana Bogodorova
Giusseppe Laera
Joan Russiñol Mussons